Multifamily Performance Program

New Construction Component

Open-Wall Checklist

This checklist shall be completed for all projects by the field representative at the Open-Wall inspection stage and submitted with the Open-Wall submittal.

Name of Project: Partner Firm: Inspector Name: Inspection Date:

| Domestic Water Heating |  |  |  |  |
| --- | --- | --- | --- | --- |
| Minimum Performance Standard | Verified in Field | Verified on Plans(1), (2) | N/A | Area Inspected or Location in Plans If N/A, provide explanation |
| For circulating systems, piping carrying liquid or steam with temperatures greater than 105°F has a min. of 1” of insulation. Pipes over 1.5” in diameter have a min. of 1.5” of insulation. |  |  |  |  |

| Garages and Sidewalks |  |  |  |  |
| --- | --- | --- | --- | --- |
| Minimum Performance Standard | Verified in Field | Verified on Plans(1), (2) | N/A | Area Inspected or Location in Plans If N/A, provide explanation |
| Attached garages are fully compartmentalized and air sealed from rest of the building. All pipe and conduit penetrations are sealed with material compatible with the surface and resilient to temperature fluctuations. |  |  |  |  |
| Garages are not heated for comfort or to prevent pipes from freezing. Piping design and layout shall locate piping within conditioned spaces or group and properly insulate them to prevent freezing. |  |  |  |  |

(1) NYCECCC 1RCNY 5000-01 Construction document approval requirements for compliance with the New York City Energy Conservation Code; (g) `Supporting documentation’

(2) 2010 NYSECCC Section 103 Construction Documents; 103.2 `Information on construction documents’

| Envelope |  |  |  |  |
| --- | --- | --- | --- | --- |
| Minimum Performance Standard | Verified in Field | Verified on Plans(1), (2) | N/A | Area Inspected or Location in Plans If N/A, provide explanation |
| The Partner’s Project Manager/inspector has reviewed the on-site construction drawings to confirm applicable Component MPS are included on the drawings/blueprints. |  |  |  |  |
| The building has a continuous, unbroken air barrier separating the conditioned space of the building from: |  |  |  |  |
| The exterior |  |  |  |  |
| Unconditioned spaces within the building |  |  |  |  |
| Non-residential spaces |  |  |  |  |
| Elevator shafts |  |  |  |  |
| Vented mechanical rooms |  |  |  |  |
| Mechanical chases opening to unconditioned spaces |  |  |  |  |
| Garages or other vehicle/equipment storage facilities |  |  |  |  |
| Apartments are sealed to reduce air exchange between the apartment and outside as well as the apartment and other adjacent spaces. |  |  |  |  |
| All Insulation is installed to RESNET Grade I rating, or Grade II if continuous insulation is used. |  |  |  |  |
| *For steel-framed and metal buildings, continuous exterior insulation is required. For mass or masonry buildings with metal framing, continuous interior or exterior insulation is required. (*Prescriptive Path: Minimum R-3 insulation required) |  |  |  | FORMTEXT |
| Specified windows are double or triple-pane, with low-emissivity glass or coatings, and comply with NYS ECCC. Window frames are separated from conductive framing with insulation designed to serve as a thermal break. |  |  |  |  |
| Ductwork penetrations are sealed at the roof curb to prevent air leakage through the duct system and/or the building envelope. |  |  |  |  |

| Heating and Cooling Distribution |  |  |  |  |
| --- | --- | --- | --- | --- |
| Minimum Performance Standard | Verified in Field | Verified on Plans(1), (2) | N/A | Area Inspected or Location in Plans If N/A, provide explanation |
| Heating and cooling ductwork is sealed at all transverse joints and connections, including ductwork connections through drywall or other finish materials, using UL-181 compliant methods and materials. |  |  |  |  |
| Heating and cooling ductwork that is specified as flex duct shall follow the SMACNA installation standards for flex ducts. |  |  |  |  |
| *Heating and cooling ductwork is insulated to a minimum R-4 in conditioned spaces and R-6 in unconditioned spaces. Ducts are insulated and sealed to the requirements of NYS ECCC. (*Prescriptive Path: Minimum R-8 in unconditioned spaces) |  |  |  |  |
| Piping carrying liquid or steam with temperatures < 60°F or >105°F are insulated in accordance with NYS ECCC. |  |  |  |  |

| VENTILATION AND INFILTRATION |  |  |  |  |
| --- | --- | --- | --- | --- |
| Minimum Performance Standard | Verified in Field | Verified on Plans(1), (2) | N/A | Area Inspected or Location in Plans If N/A, provide explanation |
| Outdoor air is provided to each unit directly from the outdoors. Systems that rely on transfer air from pressurized hallways or corridors, adjacent dwelling units, attics, etc. are prohibited. Projects using exhaust ventilation systems specify how outside air is delivered at the flow rate required by ASHRAE 62.2-2007. |  |  |  |  |
| Ventilation system ductwork is sealed at all transverse joints and connections including boot to wall/ceiling connections through drywall using UL-181 compliant materials and methods. |  |  |  |  |

I confirm that these Minimum Performance Standards have been verified, and that the information provided in this document accurately reflects the project’s design and/or construction.  Furthermore, I understand that falsely reporting these standards could jeopardize the project’s eligibility for Program incentives and/or the ENERGY STAR label and Partner Status.

Print of Partner’s Field Inspector Name		Date

Partner’s Field Inspector Signature